Quality Assurance / Quality Control (QA-QC) Plan

Green Communications Contracting LLC  ·  Effective April 9, 2026

1.  Quality Policy

We deliver every project to specification, on schedule, with zero defects at final inspection. Quality is built into every phase of our work — from material procurement through final certification testing.

2.  Applicable Standards

ANSI/TIA-568.2-D (Balanced Twisted-Pair Cabling)

ANSI/TIA-568.3-D (Optical Fiber Cabling)

ANSI/TIA-606-C (Administration Standard for Telecommunications Infrastructure)

BICSI TDMM 15th Edition

NEC / NFPA 70 (as applicable to low-voltage)

OSHA 29 CFR 1926 (Construction Safety)

Project-specific specifications and drawings

3.  QA/QC Responsibilities

| Role | Responsibility |
| --- | --- |
| QA Manager (Nathan Morris) | Oversees quality program, conducts inspections, reviews test results, approves corrective actions |
| Field Installers | Follow installation standards, perform self-inspections, report deficiencies |
| CEO (Kaitlyn Morris) | Reviews quality metrics, approves program updates |

4.  Pre-Installation QC

Before we begin installation on any project, we complete the following:

Review all project drawings, specifications, and addenda.

Verify material approvals are complete.

Confirm cable and connector types match the spec.

Inspect all materials upon delivery for damage and correct part numbers.

Conduct a site walk to verify pathway routing and TR locations match drawings.

Brief the crew on project-specific quality requirements.

5.  Installation QC

During installation, we maintain quality through:

Cable handling — We maintain bend radius per manufacturer specs, do not exceed pulling tension limits, and protect all cable from damage.

Termination — We terminate all copper to T568B (unless spec requires T568A) and maintain pair twist to within 0.5" of termination point.

Fiber — We clean and inspect all connectors before mating; we fusion-splice per manufacturer procedures.

Pathway — We install J-hooks at maximum 48" intervals, maintain cable fill ratios per NEC, and separate low-voltage from power per code.

Labeling — We label both ends of every cable per ANSI/TIA-606-C before testing.

Daily inspection — Our field supervisor inspects all work completed each day and corrects deficiencies before proceeding.

6.  Testing & Certification

We test 100% of all copper links using Fluke DSX-8000.

We test 100% of all fiber links using Fluke CertiFiber Pro.

We test to the permanent link model for copper and the channel model when required.

Every link must pass — we do not sample.

Failed links are re-terminated and re-tested until they pass.

We export all test results via Fluke LinkWare and deliver PDF + .flw files.

7.  Labeling Standards

We follow ANSI/TIA-606-C at both ends of every cable.

Cable IDs match the cable schedule and as-built documentation.

We use machine-printed labels (no handwriting).

Labels are applied to cables, patch panels, faceplates, and racks.

8.  Security / Access Control QC (Division 28)

We verify all reader, camera, and contact locations match drawings before rough-in.

We confirm cable types match spec (shielded where required).

We test continuity on all security cabling before device installation.

We coordinate with the security integrator for device programming and commissioning (programming is by others).

9.  Closeout Documentation

At project completion, we deliver:

100% Fluke test results (PDF + LinkWare)

As-built cable schedule with actual measured lengths

As-built rack elevation drawings

Label matrix

Product data sheets and manufacturer warranty certificates

O&M manual

10.  Non-Conformance & Corrective Action

When we identify a deficiency:

We document the issue (location, description, root cause).

We implement corrective action immediately.

We re-inspect and re-test after correction.

We record the resolution in our project quality log.

We review recurring issues at the end of each project to update our procedures.

Prepared by: GCC Estimating Department  ·  Contact: kaitlyn@greencommllc.com  ·  (636) 224-8192