CABLE SCHEDULE

{{JOB NAME}} — {{GC NAME}} — {{SITE CITY, STATE}}

INTERNAL DOCUMENT — GCC EYES ONLY Contains internal cost rates, margin analysis, and strategy. Never attach to a proposal, quote, or email to a GC, Owner, or Subcontractor.

PURPOSE

Single source of truth for field crew on every cable installed on this job. Captures site-wide cable spec, color discipline, service loops, wall plates, TR/IDF/MDF buildouts, and LF totals. Reconciles with BTQ quantities and Drop Counts. Updated through bid + construction.

1.  Site-Wide Cable Spec

| Discipline | Cable | Jacket Color | Connector | Test Class |
| --- | --- | --- | --- | --- |
| Data (horizontal) | Cat6A plenum (GCC baseline — never Cat6) | Blue | RJ-45 8P8C | Class EA |
| Voice (horizontal) | Cat6A plenum | White | RJ-45 8P8C | Class EA |
| CCTV | Cat6A plenum | Green | RJ-45 / BNC where analog | Class EA |
| ACS (readers, REX, door contacts) | Cat6A plenum + 22/4 comp | Red | Termination per mfr | Continuity + polarity |
| Intercom / paging | Cat6A plenum | {{per spec}} | RJ-45 | Class EA |
| Fiber backbone | OS2 SM 12-strand (min) | Yellow | LC / SC fusion | OTDR bidir + insertion |
| Fiber horizontal (fiber-to-desk) | OM4 MM 2-strand | Aqua | LC fusion | OTDR + insertion |
| Coax (AV / CATV feeds) | RG-6 quad-shield plenum | Black | F-type compression | DC continuity |

Included Upgrades (GCC baseline on every bid)

Cat6A plenum on every data drop — included at no upcharge to the GC, even when the base spec calls for Cat6. Cat6 substitute for Cat6A is NEVER offered.

TIA-606-C Class 3 labeling on both ends of every cable.

Fluke DSX-8000 Class EA certification on every Cat6A drop. LinkWare PDF at closeout.

Lifetime GCC workmanship warranty on every cable.

2.  Service Loops & Slack

| Location | Service Loop Length | Coiled / Routed |
| --- | --- | --- |
| MDF (head-end) | 10 ft | Coiled above rack, velcro-bound |
| IDF (intermediate) | 10 ft | Coiled above rack, velcro-bound |
| Endpoint (WAP, camera, wall plate) | 3 ft | Looped above ceiling tile |
| Elevator shaft (per cab) | 5 ft at MDF + 5 ft at cab | Coiled, secured with zip ties (no tape) |
| Roof-top camera / device | 6 ft | Inside pathway before roof penetration |

Service loops are non-negotiable minimums. When pathway doesn't allow, crew documents deviation on the as-built. Never cut below these lengths.

3.  Wall Plates & Connectors

| Location Type | Plate Style | Port Count | Labels |
| --- | --- | --- | --- |
| Workstation | Single-gang flush, white | 2 (1 blue data, 1 white voice) | Room-port format per TIA-606-C |
| WAP | Ceiling mount (if exposed); above-tile flush (standard) | 1 (blue data) | WAP-# label on cable + plate |
| Camera drop | Ceiling mount if exposed; plate above tile | 1 (green CCTV) | CAM-# label |
| ACS reader | Single-gang, color per finish schedule | 1 (red ACS + 22/4) | DR-# label |
| Conference room | Single-gang flush, white | {{spec count}} | Room-port |
| Kiosk / wall display | Single-gang flush, white | 1 (blue data) | KIOSK-# |

4.  TR / IDF / MDF Buildouts

MDF (head-end)

42U floor-standing rack (or as specified) — ladder rack overhead, vertical cable managers both sides.

3/4" fire-treated plywood backboard, painted dove-gray, floor-to-ceiling wall.

#6 AWG grounding buss bar at 18" AFF, tied to building ground electrode (verify with EC).

Horizontal patch panels: 48-port Cat6A, 1U each, populated per drop count.

Fiber housing: 4U LIU/FDF with LC couplers, populated per backbone strand count.

PDU: 20A L5-20R, minimum 2 per rack (A+B feed if redundant power available).

UPS: sized per active-equipment load (sized at closeout, not base bid).

IDF (intermediate)

Wall-mount rack (typ.) or 42U floor-standing (on spec).

Plywood backboard, buss bar, PDU — same spec as MDF.

Fiber backbone termination: LIU sized to strand count + 100% spare capacity.

Horizontal patch panels sized to drop count per closet.

Cable management

Vertical managers both sides of rack.

Horizontal manager 1U between every patch panel.

Velcro bundles only — no zip ties on horizontal cable in rack.

Service loops dressed overhead, coiled, velcro-bound.

5.  Cable LF Totals

| Cable Type | Drops / Strands | Avg Run | Waste % | Total LF | Boxes / Reels |
| --- | --- | --- | --- | --- | --- |
| Cat6A plenum (data) | {{}} | {{avg}} ft | 10% | {{}} | {{}} |
| Cat6A plenum (voice) | {{}} | {{avg}} ft | 10% | {{}} | {{}} |
| Cat6A plenum (CCTV) | {{}} | {{avg}} ft | 10% | {{}} | {{}} |
| Cat6A plenum (ACS) | {{}} | {{avg}} ft | 10% | {{}} | {{}} |
| Fiber OS2 SM backbone | {{}} | {{}} ft | 5% | {{}} | {{}} |
| 22/4 composite (ACS) | {{}} | {{}} ft | 10% | {{}} | {{}} |
| RG-6 plenum coax | {{}} | {{}} ft | 10% | {{}} | {{}} |

Box count: ⌈total LF / 1000⌉ × 1.05 (5% safety stock per Conservative Labor Rule). Fiber reel count: round up to next standard reel length carried by supplier.

6.  Field Rules (for installers)

No cable touches a ceiling tile, pipe, sprinkler, or lighting fixture. All supported by J-hook, cable tray, or EMT.

J-hook spacing: max 4 ft center-to-center above accessible ceiling.

Bend radius: Cat6A = 4× cable OD minimum (typically 1"); fiber = 10× cable OD minimum.

Pull tension: Cat6A max 25 lbf; fiber max 600 lbf (long-term), 200 lbf (pull).

Firestop: installed by others (GCC does not carry firestop in base bid — see Bid Proposal §7.C).

Labels: printed (Brother P-touch or equivalent) — hand-written labels never accepted at closeout.

Every cable tested at termination; fails get reworked on the spot, not deferred.

Daily close-out: crew logs installed cable count + location in Field Guide.

7.  Reconciliation Sources

Drop counts: `{{Job}}/Internal/Drop Counts.pdf`

BTQ quantities: `{{Job}}/Internal/BTQ.xlsx` — cable subtotal must match §5 total LF.

Labor Plan: `{{Job}}/Internal/Labor Plan.xlsx` — per-drop hours reconcile with Master Catalog Services sheet.

Field Guide: `{{Job}}/Internal/Field Guide.pdf` — installer's floor-by-floor checklist reads from this doc.