Standards

{{SITE_NAME}} — {{CITY_STATE}}

Warranty  ·  Testing & Certification  ·  Compliance

LIFETIME WORKMANSHIP — TRANSFERS WITH THE PROPERTY

1.  Three-Tier Warranty

GCC warrants its installed low-voltage infrastructure at three levels. Each tier is distinct in duration and pass-through posture. Together they deliver the strongest coverage in the KCMO + STL Div 27/28 market.

| Tier | Scope | Term |
| --- | --- | --- |
| Tier 1 — Lifetime Workmanship | All GCC installation labor. Covers wire-map errors, termination defects, labeling errors, physical install quality. | Lifetime — transfers with the property. |
| Tier 2 — 5-Year GCC-Furnished Hardware | GCC-furnished passive hardware (patch panels, jacks, faceplates, cable, fiber housings, racks, ladder racking) installed by GCC. | 5 years from substantial completion. |
| Tier 3 — Manufacturer Pass-Through | All active equipment and any component carrying a manufacturer warranty. GCC processes RMAs on behalf of owner at no additional cost during the manufacturer period. | Per manufacturer — GCC facilitates. |

What the Lifetime Workmanship Warranty does

Covers GCC's physical install: pull, dress, terminate, label.

Follows the property — future owners inherit the coverage on transfer of title, no paperwork.

GCC re-pulls, re-terminates, and re-certifies failing infrastructure on a service ticket at no cost for life.

Excludes damage from third-party work, environmental events, or owner modifications (Bid Proposal Exclusion §7.K).

2.  Testing & Certification

Every copper drop and every fiber strand installed by GCC is certified before the substantial completion punch closes. Testing is evidence-based; LinkWare PDF reports are delivered at closeout.

Copper — every drop, Permanent Link test

Instrument: Fluke Networks DSX-8000 CableAnalyzer — the accepted industry standard.

Test class: Class EA (Cat6A) on every drop — GCC baseline is Cat6A plenum; Cat6 substitute is not offered.

Parameters reported: wire-map, length, insertion loss, return loss, NEXT, PS-NEXT, ACRF, PS-ACRF, propagation delay, delay skew.

Fail = re-terminate + re-certify. Drop is not closed until it passes.

Fiber — every strand, bidirectional

Bidirectional OTDR trace for each strand.

OLTS insertion loss verification end-to-end.

Fusion splice verified at ≤0.1 dB (typical ≤0.05 dB in-house).

Reporting

100% of installed infrastructure certified — no sampling. Every drop. Every strand.

LinkWare PDF reports delivered to GC and owner at closeout, indexed by Class 3 label.

Reports archived by GCC for life-of-installation reference.

3.  Compliance Standards

All work executed in compliance with the following published standards as a minimum. Stricter project spec governs when applicable.

| Standard | Scope |
| --- | --- |
| TIA-568.2-D | Balanced twisted-pair telecommunications cabling |
| TIA-568.3-D | Optical fiber cabling components |
| TIA-569-D | Telecommunications pathways and spaces |
| TIA-606-C | Administration — Class 3 labeling (GCC default on every job) |
| TIA-607-D | Generic telecommunications bonding and grounding |
| BICSI TDMM | Telecommunications Distribution Methods Manual, 15th Edition |
| NEC / NFPA 70 | National Electrical Code — applicable low-voltage sections |
| OSHA 29 CFR 1926 | Construction safety |

4.  Closeout Deliverables

Every GCC job closes with the following documentation package delivered to GC and owner.

LinkWare PDF test reports for every drop and every fiber strand, indexed by TIA-606-C Class 3 label.

As-built drawings reflecting any field routing deviations, cable counts per run, and MDF / IDF equipment layout.

Labeling schedule — every label printed, every drop accounted for.

Warranty registration package: Tier 1 workmanship transfer letter, Tier 2 5-year hardware registration, Tier 3 manufacturer warranty cards.

Owner training sign-off if in-scope per job.

5.  Field Staff Certifications

OSHA 10-hour construction safety — minimum for every field tech.

OSHA 30-hour construction safety — every foreman.

BICSI Installer Level 1 or 2 — every terminating tech.

Manufacturer-specific installation training where the cable system requires it (Panduit, CommScope, Corning).

Background check clearance on demand for K-12, healthcare, and federal sites.